## Load Shed
Cal Poly State University, San Luis Obispo
Energy Management System Load Shed Plan - updated 9/2011
Priority to shed | Building | Unit | Point Name | Area Served | kW | special events | computer labs | operable windows | Effect of Curtailment
1 | 70 Facility Services | Chiller | na | Facility Services office, warehouse, mailroom | 30 |  |  | yes | No heat, ventilation or cooling - temps may reach 85 or 90 degrees.
1 | 43 Rec Sports | AH4 | RS4CMD | Main Gym | 43 | yes |  |  | No heat or ventilation to main gym- minimal impact except during very cold or very hot weather or during high occupancy events. Air conditioning to front offices needs to be turned off by users.
1 | 43 Rec Sports | AH1 | RS1CMD | Aerobics Room | 4 |  |  |  | No heat or ventilation to aerobics room - minimal impact except during very cold or very hot weather.
1 | 43 Rec Sports | AH8 | RS8CMD | Raquetball Courts | 12 |  |  |  | No heat or ventilation to raquetball courts - minimal impact except during very cold or very hot weather.
1 | 44 Rec Sports | AH5 | RA5CMD | Martial Arts Room | 6 |  |  |  | No heat or ventilation to martial arts room - minimal impact except during very cold or very hot weather.
1 | 43-1 PE Tower | AC1 | RC1CMD | 4th floor computer lab - room 458 | 7 |  | yes | yes | No heat, ventilation or cooling - temps may reach 85 or 90 degrees.
1 | 43-1 PE Tower | AC2 | RC2CMD | 1st, 2nd, 4th floor labs and offices | 9 |  |  | yes | No heat, ventilation or cooling - temps may reach 85 or 90 degrees.
1 | 06 PAC | Chill water | FLDVLV | Main hall, stage, lobbies, rehearsal pavillion, dressing rooms, green room | 225 | yes |  |  | No cooling - main hall may reach 80 degrees, lobby may reach 95 degrees.
1 | 42 Mott | Gym AH1, AH2 | YSOCC | Main gym | 48 | yes |  |  | No heat or ventilation - minimal impact except during very cold or very hot weather or during high occupancy events.
1 | 65 UU | AH6 | USFAN6 | Chumash Auditorium | 27 | yes |  |  | No heat or ventilation - minimal impact except during very cold or very hot weather or during high occupancy events.
1 | 20 Eng East | Chill water | EE24CO EE26CO EE27CO EE34CO | room 124, 126, 127, 134 | 5 |  | yes | yes | No cooling to rooms 124, 126, 127, 134 - temps may reach 85 or 90 degrees.
1 | 26 Graphic Arts | Chill water | PCOOL | Entire building except for computer labs with DX units | 35 |  |  | yes | No cooling - temps may reach 85 or 90 degrees.
1 | 19 Dining | Chill water | ICHWSS | Entire building | 35 |  |  | yes | No cooling - temps may reach 85 or 90 degrees.
1 | 124 Student Services | Chill water | STCHWP STCHWV | Entire building | 14 |  |  |  | No cooling - temps may reach 85 or 90 degrees.
1 | 40 MEP | Chill water | CMECVP | MEP, MESA | 6 |  | yes |  | No cooling - temps may reach 85 degrees.
1 | 34 Dexter | AH6 cooling | DS6CLG | Room 227, 228 | 6 |  |  |  | No cooling - temps may reach 85 degrees.
1 | 65 UU | Chill water | UCCMD | Entire building | 110 | yes |  |  | No cooling - temps may reach 85 degrees.
1 | 44/45 Theater, Music | Chill water | MCOOL | Entire building | 48 | yes |  |  | No cooling - temps may reach 85 degrees.
2 | 06 PAC | AH1 | FA1TOD | Main hall | 38 | yes |  |  | No heat, ventilation or cooling - temps may reach 85 or 90 degrees. Minimal impact if no event.
2 | 06 PAC | AH2 | FA2TOD | Main stage | 15 | yes |  |  | No heat, ventilation or cooling - temps may reach 85 or 90 degrees. Minimal impact if no event.
3 | 06 PAC | AH4 | FA4TOD | Lobbies | 45 | yes |  |  | No heat, ventilation or cooling - temps may reach 90 or 95 degrees. Minimal impact if no event.
2 | 35 Kennedy Library | AH2 | LBAH2F | Interior space, SE quadrant | 6 |  |  |  | No ventilation to interior spaces - temps may reach 85 degrees.
2 | 35 Kennedy Library | AH3 | LBAH3F | Interior space, SW quadrant | 10 |  |  |  | No ventilation to interior spaces - temps may reach 85 degrees.
2 | 35 Kennedy Library | AH4 | LBAH4F | Interior space, NW quadrant | 26 |  |  |  | No ventilation to interior spaces - temps may reach 85 degrees.
2 | 07 ATL | AC1 | ATSF1 | Room 2 | 20 | yes |  |  | No heat, ventilation or cooling to room 2 - temp may reach 85 or 90 degrees.
2 | 44 Theater | AH3 | MS3CMD | Little theater | 10 | yes |  |  | No heat, ventilation or cooling to little theater. Temps may reach 85 degrees.
2 | 105 Trinity | CH1 | TRCLG | Entire building | 45 |  |  | yes | No cooling - temps may reach 85 or 90 degrees.
2 | 106 Santa Lucia | CH1 | SLCLG | Entire building | 45 |  |  | yes | No cooling - temps may reach 85 or 90 degrees.
2 | 107 Muir | CH1 | MRCLG | Entire building | 45 |  |  | yes | No cooling - temps may reach 85 or 90 degrees.
2 | 108 Sequoia | CH1 | SQCLG | Entire building | 45 |  |  | yes | No cooling - temps may reach 85 or 90 degrees.
2 | 109 Fremont | CH1 | FTCLG | Entire building | 45 |  |  | yes | No cooling - temps may reach 85 or 90 degrees.
2 | 110 Tenaya | CH1 | TNCLG | Entire building | 45 |  |  | yes | No cooling - temps may reach 85 or 90 degrees.
2 | 105 Trinity | room fan units | TROCC | All resident rooms | 10 |  |  | yes | No ventilation - temps may reach 85 or 90 degrees.
2 | 106 Santa Lucia | room fan units | SLOCC | All resident rooms | 10 |  |  | yes | No ventilation - temps may reach 85 or 90 degrees.
2 | 107 Muir | room fan units | MROCC | All resident rooms | 10 |  |  | yes | No ventilation - temps may reach 85 or 90 degrees.
2 | 108 Sequoia | room fan units | SQOCC | All resident rooms | 10 |  |  | yes | No ventilation - temps may reach 85 or 90 degrees.
2 | 109 Fremont | room fan units | FTOCC | All resident rooms | 10 |  |  | yes | No ventilation - temps may reach 85 or 90 degrees.
2 | 110 Tenaya | room fan units | TNOCC | All resident rooms | 10 |  |  | yes | No ventilation - temps may reach 85 or 90 degrees.
2 | 171A PCV | A049-AC | See next column | 171A_A049-AC.OCC (AC-1-4-1) | 35 |  |  |  | No cooling - temps may reach 85 or 90 degrees.
2 | 171A PCV | A020-AC | See next column | 171A_A020-AC.OCC (AC-1-2-1) | 45 |  |  |  | No cooling - temps may reach 85 or 90 degrees.
2 | 171A PCV | A065-AC | See next column | 171A_A065-AC.OCC (AC-1-1-1) | 13 |  |  |  | No cooling - temps may reach 85 or 90 degrees.
2 | 171H PCV | H136-AC | See next column | 171H_H136-AC.OCC (AC-4) | 1 |  |  |  | No cooling - temps may reach 85 or 90 degrees.
3 | 171B PCV | B003-AC | See next column | 171B_B003-AC.OCC Einstein Bagel | 22 |  |  |  | No cooling - temps may reach 85 or 90 degrees. Food Production Areas
3 | 171B PCV | B002-AC | See next column | 171B_B002-AC.OCC Jamba Juice | 12 |  |  |  | No cooling - temps may reach 85 or 90 degrees. Food Production Areas
3 | 171I PCV | I006-AC | See next column | 171I_I006-AC.OCC Peet Coffee | 19 |  |  |  | No cooling - temps may reach 85 or 90 degrees. Food Production Areas
3 | 20 Eng East | room fan units | EEFANS | Entire building | 15 |  | yes | yes | No ventilation - temps may reach 85 or 90 degrees.
3 | 35 Kennedy Library | AH1 | LBAH1F | Interior space, NE quadrant, reserve room | 32 |  | yes |  | No ventilation to interior spaces including reserve room - temps may reach 85 degrees.
3 | 38 COSAM | CH1 | TCHSYS | Cosam labs 121,123,131,135 | 20 |  | yes |  | No cooling - temps may reach 85 or 90 degrees.
3 | 112 Vista Grande | Chill water | VCHWP1 | Entire building | 16 |  |  |  | No cooling - temps may reach 85 or 90 degrees. Kitchen temps may reach 95 degrees.
3 | 03 Business | CH1 | BCWSYS | 3rd, 4th, and 5th floors | 45 |  | yes |  | No cooling - temps may reach 85 or 90 degrees. Server in 301B will still have cooling.
3 | 01 Admin | Chill water | ADCHWP ACWV | Entire building | 57 |  |  |  | No cooling - temps may reach 85 or 90 degrees.
3 | 27 Health Center | Chill water | HACHWP | Entire building. Lab and pharmacy will still have cooling. | 30 |  |  |  | No cooling - temps may reach 85 or 90 degrees.
4 | E4/E3 & Bonderson | Chill water | E4C1EN | No cooling E3, E4 and Bonderson | 159 |  | Various |  | No cooling - temps may reach 85 or 90 degrees. No chiller, pump and cooling tower
4 | 40 Central Plant | Chiller Plant | CPCHEN | Aux equipment - all chill water buildings have already been curtailed | 60 | yes | yes |  | No cooling - temps may reach 85 or 90 degrees.
5 | 10 Ag Erhart | AH1, AH2 | GS1CMD GS2CMD | Entire building | 22 |  | yes | yes | No ventilation - temps may reach 85 degrees. Air conditioning to computer labs and offices needs to be turned off by users.
5 | 22 English | AH1 | NS1CMD | Entire building | 12 |  |  | yes | No ventilation - temps may reach 85 or 90 degrees.
5 | 38 Math/Sci | AH1, AH2 | HS1CMD TS2CMD | Entire building except for COSAM labs | 40 |  |  | yes | No ventilation - temps may reach 85 or 90 degrees.
5 | 52 Science | AH units | SEMZ1F SEMZ2F SBM1CD SBM2CD SBDXC | B wing, E wing | 19 |  |  | yes | No ventilation - temps may reach 85 or 90 degrees. No cooling to labs B11, B12.
5 | 21 Eng West | AH1-5 | ES1CMD ES2CMD ES3CMD ES4CMD ES5CMD | Entire building | 69 |  |  | yes | No ventilation - temps may reach 85 or 90 degrees.
5 | 33 Fisher | AH1 | LS1CMD | Entire building | 46 |  |  | yes | No ventilation - temps may reach 85 or 90 degrees. No cooling to 4th floor rooms. Chilled water will remain on to growth chambers.
5 | 53 Sci North | AH1 | SS1CMD | Entire building | 52 |  |  | yes | No ventilation - temps may reach 85 or 90 degrees.
5 | 03 Business | AH1, AH2 | BS1CMD BS2CMD | 1st and 2nd floors | 19 |  |  |  | No ventilation - temps may reach 85 or 90 degrees.
5 | 02 Education | AH9 | BS9CMD BR9CMD | Rooms 126, 127, and 2nd floor | 9 |  |  | yes | No ventilation - temps may reach 85 or 90 degrees.
6 | 13 Engineering | HV9 | ESHV9F | Rooms 117, 118, 120, 121, 123 | 5 |  |  | yes | No ventilation - temps may reach 85 or 90 degrees.
6 | 45 Music | S1 | MS1CMD | Entire building except for 216, 218 | 19 |  |  | yes | No ventilation - temps may reach 85 or 90 degrees.
6 | 15 FAB | heating system | FAOCC | Entire building | 1 |  |  | yes | No affects.
6 | 35 Kennedy Library | HV1 | LBHV1F | Enntire building perimeter. Air handling units AH1-AH4 will remain running for ventilation | 5 |  |  | yes | Reduced ventilation, no heat to perimeter areas - temps may reach 85 or 90 degrees.
6 | 35 Kennedy Library | HV2 | LBHV2F |  | 5 |  |  | yes | Reduced ventilation, no heat to perimeter areas - temps may reach 85 or 90 degrees.
6 | 35 Kennedy Library | HV3 | LBHV3F |  | 3 |  |  | yes | Reduced ventilation, no heat to perimeter areas - temps may reach 85 or 90 degrees.
6 | 35 Kennedy Library | HV4 | LBHV4F |  | 5 |  |  | yes | Reduced ventilation, no heat to perimeter areas - temps may reach 85 or 90 degrees.
6 | 35 Kennedy Library | HV5 | LBHV5F |  | 10 |  |  | yes | Reduced ventilation, no heat to perimeter areas - temps may reach 85 or 90 degrees.
6 | 35 Kennedy Library | HV6 | LBHV6F |  | 5 |  |  | yes | Reduced ventilation, no heat to perimeter areas - temps may reach 85 or 90 degrees.
6 | 35 Kennedy Library | HV7 | LBHV7F |  | 5 |  |  | yes | Reduced ventilation, no heat to perimeter areas - temps may reach 85 or 90 degrees.
6 | 06 PAC | AH5 | FS5CMD | Dressing Rooms | 9 | yes |  | no | No ventilation - only if not in use.
6 | 06 PAC | AH3 | VAV Boxes | Pavillion | 10 | yes |  | no | No ventilation - only if not in use.
6 | 06 PAC |  | FCHWP5 | Founder's Room | 1 | yes |  | no | No ventilation - only if not in use.
6 | Lassen | HWP1, 2 | LAHWP1 LAHWP2 | Hot water pumps | 1 |  |  |  | Affects domestic hot water storage after 2 hours.
6 | Diablo | HWP1, 2 | DBHWP1 DBHWP2 | Hot water pumps | 1 |  |  |  | Affects domestic hot water storage after 2 hours.
6 | Palomar | HWP1, 2 | PLHWP1 PLHWP2 | Hot water pumps | 1 |  |  |  | Affects domestic hot water storage after 2 hours.
6 | Shasta | HWP1, 2 | SHHWP1 SHHWP2 | Hot water pumps | 1 |  |  |  | Affects domestic hot water storage after 2 hours.
6 | 40 Boiler Plant | Boiler 1,2,3 | CPB101 CPB201 CPB301 | Boilers | 25 |  |  |  | If operating conditions permit.
6 | 40 Boiler Plant | Primary pump 1,2,3 | CPHWP1 CPHWP2 CPHWP3 |  | 15 |  |  |  | If operating conditions permit.
Maximum possible electrical load shed by EMS |  |  |  |  | 2166 | kW
Note on F12: Dennis K. Elliot: estimated
Note on F15: Dennis Elliot: estimated
Note on F16: Dennis Elliot: estimated
Note on F17: Dennis K. Elliot: Includes CHW pump and portion of load on central plant chillers.
Note on F18: Dennis K. Elliot: Includes CHW pump and portion of load on central plant chillers.
Note on F19: Dennis K. Elliot: Includes CHW pump and portion of load on central plant chillers.
Note on F21: Dennis K. Elliot: Includes CHW pump and portion of load on central plant chillers.
Note on F22: Dennis K. Elliot: Includes CHW pump and portion of load on central plant chillers.
Note on F31: Dennis K. Elliot: Peak load 60 kW
Note on F32: Dennis K. Elliot: Peak load 60 kW
Note on F33: Dennis K. Elliot: Peak load 60 kW
Note on F34: Dennis K. Elliot: Peak load 60 kW
Note on F35: Dennis K. Elliot: Peak load 60 kW
Note on F36: Dennis K. Elliot: Peak load 60 kW
Note on F50: Dennis Elliot: estimated
Note on F53: Dennis K. Elliot: Includes CHW pump and portion of load on central plant chillers.
Note on F55: Dennis K. Elliot: Includes CHW pump and portion of load on central plant chillers.
Note on F56: Dennis K. Elliot: Includes CHW pump and portion of load on central plant chillers.
Note on F58: Dennis K. Elliot: Base load from pumps and tower fans after all bldgs have been shed. Chiller load is 550 kW (est at 80%).